Reliability Standard Audit Worksheet

EOP-012-3 – Extreme Cold Weather Preparedness and Operations

This section to be completed by the Compliance Enforcement Authority.

| Audit ID: | Audit ID if available; or REG-NCRnnnnn-YYYYMMDD |
| --- | --- |
| Registered Entity: | Registered name of entity being audited |
| NCR Number: | NCRnnnnn |
| Compliance Enforcement Authority: | Region or NERC performing audit |
| Compliance Assessment Date(s): | Month DD, YYYY, to Month DD, YYYY |
| Compliance Monitoring Method: | [On-site Audit ¦ Off-site Audit ¦ Spot Check] |
| Names of Auditors: | Supplied by CEA |

# Applicability of Requirements

|  | BA | DP | GO | GOP | IA | LSE | PA | PSE | RC | RP | RSG | TO | TOP | TP | TSP |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| R1 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R2 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R3 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R4 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R5 |  |  | X | X |  |  |  |  |  |  |  |  |  |  |  |
| R6 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R7 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R8 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |
| R9 |  |  | X |  |  |  |  |  |  |  |  |  |  |  |  |

Legend:

| Text with blue background: | Fixed text – do not edit |
| --- | --- |
| Text entry area with green background: | Entity-supplied information |
| Text entry area with white background: | Auditor-supplied information |

Findings

(This section to be completed by the Compliance Enforcement Authority)

| Req. | Finding | Summary and Documentation | Functions Monitored |
| --- | --- | --- | --- |
| R1 |  |  |  |
| R2 |  |  |  |
| R3 |  |  |  |
| R4 |  |  |  |
| R5 |  |  |  |
| R6 |  |  |  |
| R7 |  |  |  |
| R8 |  |  |  |
| R9 |  |  |  |

| Req. | Areas of Concern |
| --- | --- |

| Req. | Recommendations |
| --- | --- |

| Req. | Positive Observations |
| --- | --- |

Subject Matter Experts

Identify the Subject Matter Expert(s) responsible for this Reliability Standard.

Registered Entity Response (Required; Insert additional rows if needed):

| SME Name | Title | Organization | Requirement(s) |
| --- | --- | --- | --- |

R1 Supporting Evidence and Documentation

R1. At least once every five (5) calendar years, each Generator Owner shall, for each of its applicable generating unit(s):

  - Calculate the Extreme Cold Weather Temperature for each of its applicable generating unit(s) and identify the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data, if necessary; and

1.1.1. If the recalculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature, the entity shall review and update its cold weather preparedness plan(s) under Requirement R4 within six (6) calendar months of the recalculation and if new corrective actions are needed, to provide the required operational capability described in Requirement R2 or R3, the entity shall develop a Corrective Action Plan within six (6) calendar months of the recalculation.

1.2. Identify generating unit(s) cold weather data, to include:

1.2.1. Generating unit(s) operating limitations in cold weather to include:

1.2.1.1. Capability and availability;

1.2.1.2. Fuel supply and inventory concerns;

1.2.1.3. Start-up issues;

1.2.1.4. Fuel switching capabilities; and

1.2.1.5. Environmental constraints.

1.2.2. Generating unit(s) minimum:

• Design temperature, and if available, the concurrent wind speed and precipitation;

• Historical operating temperature at least one hour in duration, and if available, the concurrent

wind speed and precipitation; or

• Current cold weather performance temperature determined by an engineering analysis, which

includes the concurrent wind speed and precipitation.

M1. Each Generator Owner will have evidence documenting its Extreme Cold Weather Temperature calculation, including the calculation date, source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data and design information, operating data, or engineering analysis that supports its generating unit minimum temperature.

Registered Entity Response (Required):

Question: During the calculation of ECWT, did you make any adjustments to the raw data for missing or invalid data? If Yes, provide an explanation of the adjustments for the generating unit(s).

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requested:

Provide the following evidence, or other evidence to demonstrate compliance.

Entity’s Extreme Cold Weather Temperature (ECWT) for each of its applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA).)

ECWT calculation date, sources of temperature data, and adjustments utilized for missing or invalid hourly temperature data (if applicable) for each of its applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA)).

Process documentation reflecting timing requirements and actions associated with Requirement R1.

Corrective Action Plan development and implementation timeline evidence for any Corrective Action Plan required per Requirement R1 Part 1.1.1.

Corrective Action Plan(s) for any generating unit(s) requiring a Corrective Action Plan as a result of a recalculated ECWT (subject to sampling as determined by the Compliance Enforcement Authority (CEA).

Cold weather data and generating unit(s) minimum(s) for each of its applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA)).

Updated cold weather preparedness plan if the recalculated Extreme Cold Weather Temperature (ECWT) is lower than the previous ECWT, per Requirement R1 Part 1.1.1 (subject to sampling as determined by the Compliance Enforcement Authority (CEA).

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R1

This section to be completed by the Compliance Enforcement Authority

|  | (R1.) Verify an ECWT has been calculated for each generating unit and includes calculation date(s), source(s) of temperature data, and adjustments utilized for missing or invalid hourly temperature data (if applicable) |
| --- | --- |
|  | (R1.) Verify an ECWT is calculated at least once every five calendar years for applicable generating unit(s). |
|  | (Part 1.1.1.) Verify Corrective Action Plan(s), cold weather preparedness plans, and timelines for recalculation of the ECWT (as applicable). |
|  | (Part 1.2.) Verify identification of all items under Requirement 1 Parts 1.2.1 through 1.2.5 for applicable generating unit(s). |
|  | Review processes that ensure ECWT is reviewed and recalculated at least once every five (5) calendar years for applicable generating unit(s). |
|  | (Part 1.1.1.) Verify that if the ECWT changed, that the cold weather preparedness plans were reviewed and corrective actions were updated within 6 months of a change in ECWT. |
| Note to Auditor: If the recalculated Extreme Cold Weather Temperature is lower than the previous Extreme Cold Weather Temperature (Requirement R1 Part 1.1.1), the previous and updated cold weather preparedness plan(s) or the Corrective Action Plan (and any revisions) should be provided. CMEP staff should focus on the development and implementation of the ECWT. Note that there will be the possibility of missing data utilized for the ECWT calculation. The entity may very well have an overall approach to missing data versus a unit-by-unit approach. By the nature of the percentile function, significant data loss may not change the ECWT value. The key is where the data is missing in relationship to the ECWT determined value. Missing hourly temperature values above the ECWT has limited impact to the calculation. However, missing hourly temperature values below the ECWT can impact the ECWT determined value especially if the ECWT is near 32 degrees Fahrenheit. For example, the 0.2 percentile of 50,000 hourly values equates to 100 hourly values (in this case the lowest recorded hourly temperatures.) If there is missing hourly values that would have been included in the list of 100 values, those values should be explained by the entity and may warrant further review. Missing data in the 100 values effectively has the potential of moving the ECWT value higher but that is very dependent upon the data set. A recalculated ECWT that results in the same or higher ECWT does not invoke the need to review the cold weather preparedness plan but evidence of the recalculation (e.g., source, date, etc.) should be available. For facilities that have multiple units, an ECWT for each generating unit is required. Entities can provide documentation, and should note within the documentation, that the ECWT covers all the units at a site/plant. Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R2 Supporting Evidence and Documentation

R2.	Applicable to generating units that begin commercial operation on or after October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius) shall:

- Implement freeze protection measures to protect Generator Cold Weather Critical Components that                                provide the capability to operate at the generating unit(s)’ Extreme Cold Weather Temperature with sustained concurrent twenty (20) mph (32 km/h) wind speed for (i) a period of not less than twelve (12) continuous hours, or (ii) the maximum operational duration for intermittent energy resources if less than twelve (12) continuous hours; or

- Document in a declaration, with justification, if applicable, a Generator Cold Weather Constraint in accordance with Requirement R8.

M2. 	Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R2, , or it has declared a Generator Cold Weather Constraint for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the generating unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Generator Cold Weather Constraints (if applicable).

Registered Entity Response (Required):

Question: Do you have any generating units with a commercial operation date on or after October 1, 2027 and a calculated ECWT at or below 32 degrees Fahrenheit (zero degrees Celsius) and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit? If Yes, provide a listing of the generating unit(s).

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

List of entity’s applicable generating unit(s) (with a commercial operation date on or after October 1, 2027) with an Extreme Cold Weather Temperature (ECWT) determined to be at or below 32 degrees Fahrenheit (zero degrees Celsius) that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius.)

List of implemented freeze protection measures to protect Generator Cold Weather Critical Components for applicable generating unit(s) meeting the criteria of Requirement R1 (subject to sampling as determined by the Compliance Enforcement Authority (CEA).)

Process documentation reflecting generating unit(s) performance requirements and actions associated with Requirement R2.

List of any declared Generator Cold Weather Constraints, if applicable (subject to sampling by the CEA.)

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R2

This section to be completed by the Compliance Enforcement Authority

|  | (R2.) Verify implementation of freeze protection measures for list(s) (of applicable generating unit(s) Generator Cold Weather Critical Components (subject to sampling as determined by the Compliance Enforcement Authority (CEA).) |
| --- | --- |
|  | (R2.) Review any documented assessment of the R2 criteria to which the freeze protection measures are protecting Generator Cold Weather Critical Components (e.g., How did the entity determine the freeze protection measure would withstand the R2 criteria?) |
|  | (R2.) Verify the declaration of any Generator Cold Weather Constraint (if applicable). |
| Note to Auditor: Individual generator commercial operations date determination may vary depending upon the approval process for generators. Often a commercial operations date will equate to the NCR date for a stand-alone generator (e.g., Generator 1 is the only generator for Generator Owner 1 that has an NCR date of 10/1/2024). Review footnotes within EOP-012-3 for applicability. This Requirement contains three (3) footnotes that are important to understand. The term “commercial operation” is not a Glossary Term, but it is used within the Reliability Standards. The DT felt it was necessary to include a description in Footnote 1 of the Standard to guide the industry. Canadian entities are under a different construct for the adoption of Standards and dates hard-coded within Standards so a footnote was added to provide flexibility. There may be a future Canadian variance proposed which may change the Standard. The “exemption” footnote may require additional questions to ensure applicability if a Generator Owner states they are exempt. Note that Generator Cold Weather Constraints should be in Align and would be found under the PDS module, but other options may have been used. If a Generator Cold Weather Constraint declared under Requirement R2 was denied in a prior PDS submittal], there is a need to evaluate the dates and timelines for the submittal, review, and consequential denial during the engagement. Review the Technical Rationale and Implementation Plan to evaluate dates and documentation regarding “contractually committed to design criteria” and the use of wind speed. Note that a Generator Cold Weather Constraint declaration may have been made internally by the entity but not yet submitted to the CEA (See Requirement R8 for timelines). Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R3 Supporting Evidence and Documentation

R3.	Applicable to generating unit(s) in commercial operation prior to October 1, 2027: Each Generator Owner, for each generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1, and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), shall:

- Implement freeze protection measures to protect Generator Cold Weather Critical Components that provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature; or

- Develop a Corrective Action Plan to add new or modify existing freeze protection measures to provide the capability to operate at the generating unit(s)' Extreme Cold Weather Temperature.

M3. 	Each Generator Owner will have dated evidence that demonstrates it has freeze protection measures for its generating unit(s) in accordance with R3, or it has developed a Corrective Action Plan for the identified issues. Acceptable evidence may include the following (electronic or hardcopy format): Identification of generating unit(s) minimum temperature under Requirement R1 Part 1.2.2 which is equal to or less than the unit’s Extreme Cold Weather Temperature, documentation of freeze protection measures, and Corrective Action Plan(s)

Registered Entity Response (Required):

Question: Do you have any generating units with a commercial operation date prior to October 1, 2027 and a calculated ECWT at or below 32 degrees Fahrenheit (zero degrees Celsius) and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit? If Yes, provide a listing of the generating unit(s).

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

List of entity’s applicable generating unit(s) Extreme Cold Weather Temperature (ECWT) determined to be at or below 32 degrees Fahrenheit (zero degrees Celsius) that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius).

List of implemented freeze protection measures to protect Generator Cold Weather Critical Components for applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA)).

Process documentation reflecting generating unit(s) performance requirements and actions associated with Requirement R3.

List of any Corrective Action Plans developed to provide the capability as described in Requirement R3.

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R3

This section to be completed by the Compliance Enforcement Authority

|  | (R3.) Verify implementation of freeze protection measures to protect Generator Cold Weather Critical Components for list of applicable generating unit(s). |
| --- | --- |
|  | (R3.) If freeze protections to protect Generator Cold Weather Critical Components have not yet been implemented, verify Corrective Action Plan milestones are provided and scheduled for completion (or completion dates for those already completed). Refer to Requirement R7 for timelines. |
|  | (R3.) Review any documented assessment of the selected freeze protection measures to protect Generator Cold Weather Critical Components and the resulting capability to operate the unit at ECWT (e.g., How did the entity determine the freeze protection measure would result in the unit being able to operate at ECWT?) |
| Note to Auditor: Individual generator commercial operations date (COD) determination may vary depending upon the approval process for generators. Often a commercial operations date will equate to the NCR date for a stand-alone generator (e.g., Generator 1 is the only generator for Generator Owner 1 that has an NCR date of 10/1/2024 which is same date as COD). Review footnotes for applicability. Note the list of generating units may not be all of the Generator Owners generating units because of the ECWT criteria within Requirement R3. Corrective Action Plan extensions may have been requested (review Align or other submittal process). This Requirement contains two (2) footnotes that are important to understand. Canadian entities are under a different construct for the adoption of Standards and dates hard-coded within Standards so a footnote was added to provide flexibility. There may be a future Canadian variance proposed which may change the Standard. The “exemption” footnote may require additional questions to ensure applicability if a Generator Owner states they are exempt. Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R4 Supporting Evidence and Documentation

R4.	Each Generator Owner shall implement and maintain one or more cold weather preparedness plan(s) for its generating units. The cold weather preparedness plan(s) shall include the following, at a minimum:

4.1 The lowest calculated Extreme Cold Weather Temperature for each generating unit, as determined in Requirement R1;

4.2. The generating unit cold weather data, as determined in Requirement R1, Part 1.2;

4.3. Documentation identifying Generator Cold Weather Critical Components;

4.4. Documentation of freeze protection measures implemented on Generator Cold Weather Critical            Components that includes measures used to reduce the cooling effects of wind determined necessary by the Generator Owner to protect against heat loss, and where applicable, the effects of freezing precipitation (e.g., sleet, snow, ice, and freezing rain);

4.5. Annual inspection and maintenance of generating unit(s) freeze protection measures implemented on Generator Cold Weather Critical Components.

M4.       Each Generator Owner will have evidence documenting that its cold weather preparedness plan(s) was implemented and maintained in accordance with Requirement R4. Examples of documentation to demonstrate a cold weather preparedness plan may include existing operating procedures, plans, checklists, or processes. Examples of documentation to demonstrate inspections and maintenance have been completed may include, but are not limited to, completed work order(s) from the Generator Owner’s work management system and/or freeze protection checklists identifying the measures inspected and maintained for the Generator Cold Weather Critical Components.

Registered Entity Response (Required):

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Evidence of implementation and maintenance of its cold weather preparedness plan(s) for its generating unit(s), including: updates to ECWT where recalculated ECWT, per R1, is lower than previous (Part 4.1), update of cold weather data (Part 4.2), identification of cold weather critical components (Part 4.3), implementation of freeze protection measures on Generator Cold Weather Critical Components (Part 4.4), and annual inspection and maintenance of freeze protection measures implemented on Generator Cold Weather Critical Components (Part 4.5). Evidence should include previous cold weather preparedness plan changes (as applicable).

Entity’s current cold weather preparedness plan(s) for its generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA).)

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R4

This section to be completed by the Compliance Enforcement Authority

|  | (R4.) Verify cold weather preparedness plans are implemented and maintained for the entity’s generating units (subject to sampling as determined by the Compliance Enforcement Authority (CEA)). |
| --- | --- |
|  | (R4.) Verify identification of all items under R4 are included in cold weather preparedness plans for applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA)). |
|  | (Parts 4.3 and 4.4.) Verify identification of Generator Cold Weather Critical Components and the identified freeze protection measures for the Generator Cold Weather Critical Components. |
|  | (Part 4.5.) Verify inspection and maintenance records for freeze protection measures on Generator Cold Weather Critical Components (subject to sampling as determined by the Compliance Enforcement Authority (CEA)). |
| Note to Auditor: Previous and updated cold weather preparedness plan(s) should be provided. CMEP staff should focus on the implementation and maintenance of freeze protection measures on Generator Cold Weather Critical Components especially if new generating units have been added or existing units had recent cold weather-related issues. Compliance efforts for Part 4.5 should be only on freeze protection measures applied to Generator Cold Weather Critical Components. There may be other freeze protection measures applied by a GO for a unit that are maintained for ensuring reliable operations that are not applied to Generator Cold Weather Critical Components that are not subject to compliance. Generator Owners shall include the lowest calculated Extreme Cold Weather Temperature for the unit, even where subsequent periodic re-calculations under Requirement R1 Part 1.1 cause an increase in the Extreme Cold Weather Temperature. Be sure to review footnote for applicability. The footnote reflects a need for entities to maintain their lowest ECWT determined as the ECWT for the unit and act accordingly. For example, generating units that originally had a 32 degrees Fahrenheit ECWT that subsequently recalculated to 33 degrees Fahrenheit are obligated to continue with the reliability, and subsequent compliance, obligations pursuant to the Requirements of this Standard. Please note that this Requirement is not included in the abeyance considerations for this Standard. |  |

## Auditor Notes:

R5 Supporting Evidence and Documentation

R5.	Each Generator Owner, in conjunction with its Generator Operator, shall identify the entity responsible for providing generating unit-specific training, and that identified entity shall provide annual training to the maintenance and operations personnel, as applicable, responsible for implementing the cold weather preparedness plan(s) developed pursuant to Requirement R4.

M5. 	Each Generator Operator or Generator Owner will have documented evidence that the applicable personnel completed annual training of the Generator Owner’s cold weather preparedness plan(s). This evidence may include, but is not limited to, documents such as personnel training records, training materials, date of training, agendas or learning objectives, attendance at pre-work briefings, review of work order tasks, tailboards, attendance logs for classroom training, and completion records for computer-based training in fulfillment of Requirement R5.

Registered Entity Response (Required):

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Documentation of entity responsible for training, list of personnel to be trained, employment dates for personnel to be trained, training dates, training completion status, personnel attendance records for training sessions, entity’s applicable generating unit-specific training materials, and process documents illustrating annual training has been provided (subject to sampling as determined by the Compliance Enforcement Authority (CEA)).

Cold weather preparedness plan(s) implemented pursuant to Requirement R4.

Process documentation reflecting requirements and actions for new hires associated with Requirement R5 required training.

Training on the cold weather preparedness plan including the annual inspection and maintenance of generating unit(s) freeze protection measures applied on Generator Cold Weather Critical Components.

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R5

This section to be completed by the Compliance Enforcement Authority

|  | (R5.) Verify identification of entity responsible for training, personnel to be trained, and unit-specific training materials. |
| --- | --- |
|  | (R5.) Verify training content includes information relevant to personnel responsible for the implementation of the cold weather preparedness plan(s) for their specific unit(s). |
|  | (R5.) Verify annual training requirement and delivery for personnel responsible for implementation of the cold weather preparedness plan(s). |
| Note to Auditor: If a Generator Owner or Generator Operator indicates that responsibility for training is another party, materials should still be requested and provided by the entity subject to compliance monitoring for those personnel responsible for implementing the cold weather preparedness plans for the applicable generating unit(s) in question. Please note that this Requirement is not included in the abeyance considerations for this Standard. |  |

## Auditor Notes:

R6 Supporting Evidence and Documentation

R6. Each Generator Owner shall, after experiencing a Generator Cold Weather Reliability Event at a generating unit that has a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius) as determined in Requirement R1 and that self-commits or is required to operate at or below a temperature of 32 degrees Fahrenheit (zero degrees Celsius), develop and implement a Corrective Action Plan(s) to address identified freezing issues as follows:

  - The Generator Owner shall develop a Corrective Action Plan for the generating unit that experienced a            Generator Cold Weather Reliability Event no later than prior to the first day of the first December following the Generator Cold Weather Reliability Event.

  - The Generator Owner shall conduct a review of other generating unit(s) in its fleet with the same or similar equipment as the affected generating unit to determine if any of those generating unit(s) are susceptible to the identified freezing issues. If corrective actions are needed, the Generator Owner shall develop or update a Corrective Action Plan to address the other generating unit(s). This review and, if applicable, the development or update of any Corrective Action Plan(s), shall be completed no later than 12 calendar months following the Generator Cold Weather Reliability Event.

  - For each Corrective Action Plan, the Generator Owner shall include at a minimum:

    - A summary of the identified cause(s) of the Generator Cold Weather Reliability Event, where applicable, and any relevant associated data;

    - A list of actions to add new freeze protection measures or remedy issues with existing freeze protection measures;

    - An identification of operating limitations on the generating unit(s), or impacts to the cold weather preparedness plan, if any, that would apply until implementation of the corrective action(s) identified in the Corrective Action Plan is completed;

    - A description of the updates to the cold weather preparedness plan required under Requirement R4 to identify updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures, if required; and

    - A timetable specifying that implementation of the Corrective Action Plan(s) shall be completed as follows:

      - For the generating unit experiencing the Generator Cold Weather Reliability Event, prior to the first day of the first December following the Generator Cold Weather Reliability Event.

      - For other generating unit(s) owned by the Generator Owner, within 24 calendar months of completing the review required in Part 6.2, or no later than 36 months following the Generator Cold Weather Reliability Event.

  - If a Generator Owner determines it will be unable to complete one or more of the actions in a Corrective Action Plan in accordance with the timetables specified in Requirement R6 Part 6.3.5 due to circumstances beyond its control, the Generator Owner shall submit a Corrective Action Plan extension request to the Compliance Enforcement Authority (CEA) for approval. The submitted Corrective Action Plan extension request shall include the following:

    - An explanation of the circumstances causing the delay and why those circumstances are beyond the control of the Generator Owner;

    - Revisions to the selected actions in Part 6.3.2, if any, including utilization of operating procedures, if applicable; and

    - Updated timetable for implementing the selected actions in Part 6.3.2.

  - The Generator Owner shall document in a declaration, with justification, if applicable, any Generator Cold Weather Constraint in accordance with Requirement R8, as applicable.

M6. 	Each Generator Owner will have dated evidence that it developed and implemented a Corrective Action Plan following a Cold Weather Reliability Event for applicable unit(s) in accordance with Requirement R6. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraint(s).

Registered Entity Response (Required):

Question: Have any generating units meeting the criteria in Requirement R6 experienced a Generator Cold Weather Reliability Event? If Yes, provide a summary of the Generator Cold Weather Reliability Event, the applicable generating unit(s) and the Corrective Action Plan(s). If No, describe how this was determined in the narrative section below.

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Question: Have any units experiencing a Generator Cold Weather Reliability Event required a Generator Cold Weather Constraint to be declared? If Yes, provide a summary of the Generator Cold Weather Constraint for the applicable generating unit(s). If No, describe how this was determined in the narrative section below.

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Entity’s Extreme Cold Weather Temperature for applicable generating unit(s) (subject to sampling as determined by the Compliance Enforcement Authority (CEA)).

If a Generator Cold Weather Reliability Event was experienced by an applicable generating unit(s) provide the Corrective Action Plan(s) pursuant to Requirement R6 Part 6.1. Clearly depict the status of the corrective actions within each Corrective Action Plan as well as the criteria required per Requirement R6 Part 6.3.

Process documentation, and results (including any Corrective Action Plans developed/updated including criteria required per Requirement R6 Part 6.3), of the review required pursuant to Requirement R6 Part 6.2 for other generating units.

Corrective Action Plan extension requests and associated data required within Requirement R6 Part 6.4.

Generator Cold Weather Constraint declarations and associated data (if applicable).

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R6

This section to be completed by the Compliance Enforcement Authority

|  | Review process for the identification of Generator Cold Weather Reliability Events. |
| --- | --- |
|  | Review process for development and implementation of Corrective Action Plans developed under R6 (for unit experiencing a Generator Cold Weather Reliability Event and the review of other generating units). |
|  | (Part 6.2.) Verify that applicability to similar equipment and plants was reviewed by the registered entity. |
|  | (Part 6.3.) If a Corrective Action Plan was developed, verify individual aspects of Requirement R6 Parts 6.3.1 to 6.3.5 were included (e.g., summary of identified cause(s), list of action, etc.). |
|  | (Part 6.4.) If a Corrective Action Plan was developed and corrective action(s) change or timetables are projected to exceed timelines, verify a Corrective Action Plan extension was requested and that request met Requirement R6 Parts 6.4.1 to 6.4.3. |
|  | (Part 6.5.) Verify a declaration, with justification, was documented for a Generator Cold Weather Constraint (if applicable.) |
| Note to Auditor: Some Generator Owners may not own any applicable generating unit(s) with a calculated Extreme Cold Weather Temperature at or below 32 degrees Fahrenheit (zero degrees Celsius). If a registered entity does not have any applicable generating units meeting the criteria of Requirement R6 for the development of a Corrective Action Plan, understanding how an entity would develop Corrective Action Plans is beneficial. Generator Owners Corrective Action Plans are not to exceed the timelines listed in Requirement R6 Part 6.3.5. Auditors should review the four (4) footnotes that are included in the Standard for this Requirement. The “exemption” footnote may require additional questions to ensure applicability if a Generator Owner states they are exempt. The Corrective Action Plan footnote was designed to alleviate additional administrative burden for the registered entity. Note that the initial Corrective Action Plans developed by an entity will generally only be seen by auditors during a compliance monitoring effort and could be in flux depending upon the entity’s process. The footnote for events that occur in September, October, and November is provided to give entities ample time to provide robust corrective actions to correct issues that may have caused a Generator Cold Weather Reliability Event. Most entities, if they have experienced a Generator Cold Weather Reliability Event, will act quickly to get the unit(s) back online but a more permanent fix may take longer to implement. Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R7 Supporting Evidence and Documentation

R7. Each Generator Owner that is required to develop a Corrective Action Plan under Requirements R1, R3, or R9 shall develop and implement the Corrective Action Plan in accordance with the following:

  - For each Corrective Action Plan, the Generator Owner shall include at a minimum the following:

    - A list of any actions that require new freeze protection measures, with a timetable specifying completion of such measures within 48 calendar months of completing development of the Corrective Action Plan;

    - A list of any actions that remedy issues with existing freeze protection measures with a timetable specifying completion of such measures within 24 calendar months of completing development of the Corrective Action Plan (regardless of any longer timelines in the Corrective Action Plan associated with new freeze protection measures);

    - A description of updates to the cold weather preparedness plan required under Requirement R4 to identify the updates or additions to the Generator Cold Weather Critical Components and their freeze protection measures; and

    - An identification of operating limitations on the generating unit(s), or impacts to the cold weather preparedness plan, if any, that would apply until implementation of the corrective action(s) identified in the Corrective Action Plan is completed.

  - If a Generator Owner determines it will be unable to complete one or more of the actions in a Corrective Action Plan in accordance with the timetables specified in Requirement R7 Part 7.1 due to circumstances beyond its control, the Generator Owner shall submit a Corrective Action Plan extension request to the CEA for approval. The submitted Corrective Action Plan extension request shall include the following:

    - An explanation of the circumstances causing the delay and how those circumstances are beyond the control of the Generator Owner;

    - Revisions to the selected actions in Parts 7.1, if any, including utilization of operating procedures, if applicable; and

    - Updated timetable for implementing the selected actions in Part 7.1.

  - The Generator Owner shall document in a declaration, with justification, if applicable, any Generator Cold Weather Constraint in accordance with Requirement R8.

M7. 	Each Generator Owner shall have dated evidence that it developed and implemented a Corrective Action Plan for applicable unit(s) in accordance with Requirement R7. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): Corrective Action Plan(s), completed work orders, copies of any Corrective Action Plan extension requests and supporting documentation, updated cold weather preparedness plan(s) where indicated as needed by the Corrective Action Plan, and, where applicable, declared Generator Cold Weather Constraints.

Registered Entity Response (Required):

Question: Have any Corrective Action Plans been developed pursuant to Requirements R1, R3 or R9? If Yes, provide a summary of the Corrective Action Plan(s) and the applicable generating unit(s) including source of the Corrective Action Plan (i.e., R1, R3, or R9). ☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Entity’s documented process for development of Corrective Action Plans and the applicable Corrective Action Plan(s) (including revisions) with any associated data as specified by Requirement R7 Part 7.1 (i.e., any Corrective Action Plans developed pursuant to Requirements R1, R3, or R9.)

Entity’s process for ensuring completion of Corrective Action Plan action(s) with dated implementation documentation for Corrective Action Plans.

Entity’s Corrective Action Plans for applicable generating units (subject to sampling by the CEA).

Entity’s justification (and associated documentation for Parts 7.2.1 to 7.2.3) for Corrective Action Plan(s) extension requests where the corrective action(s) change or timetable(s) exceed the timeline in Requirement R7 Part 7.1.

Entity’s declaration, and justifications for the declaration, of any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within a Corrective Action Plan. This includes those Generator Cold Weather Constraint declarations that may have not yet been submitted to the CEA pursuant to Requirement R8 timelines.

Updates (if applicable) to any declaration of Generator Cold Weather Constraints that precludes the Generator Owner from implementing selected action(s) contained within a Corrective Action Plan.

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R7

This section to be completed by the Compliance Enforcement Authority

|  | (R7.) Verify Corrective Action Plan(s) meet the criteria in the respective Requirements (R1, R3, or R9) and the timetable criteria in Requirement R7 Part 7.1. |
| --- | --- |
|  | (R7.) Verify date of Corrective Action Plan(s) development and completion (if applicable) of corrective actions. |
|  | (Part 7.2.) If one or more actions within a Corrective Action Plan cannot be completed in accordance with the timetables in Requirement 7 Part 7.1 due to circumstances beyond the control of the Generator Owner, verify a Corrective Action Plan extension request was submitted to the CEA for approval. |
|  | (Part 7.2.) For each submitted Corrective Action Plan extension request, verify it included all required information with Requirement R7 Part 7.2. |
|  | (Part 7.3.) Verify declaration, with justification, documentation for any Generator Cold Weather Constraint that precludes implementation of actions within a Corrective Action Plan. |
|  | Verify a Corrective Action Plan has been updated to reflect any Generator Cold Weather Constraint(s) (if applicable). |
| Note to Auditor: Generator Owners Corrective Action Plans are not to exceed the timelines listed in Requirement R7 without an approved extension request. Be familiar with the ERO Enterprise CAP Extension and Generator Cold Weather Constraint review process, data already provided through the process, and the resulting efforts before asking questions regarding Corrective Action Plan extension requests or Generator Cold Weather Constraints. Generator Cold Weather Constraints may have been internally developed by an entity but not yet submitted to the CEA (review timelines in Requirement R8.) Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R8 Supporting Evidence and Documentation

R8. Each Generator Owner that declares a Generator Cold Weather Constraint in accordance with Attachment 1 shall:

  - Submit its Generator Cold Weather Constraint declaration(s) to the Compliance Enforcement Authority as follows:

    - For Generator Cold Weather Constraints determined in accordance with Requirement R2 for generating unit(s) upon beginning commercial operation, submit within 15 calendar days after commercial operation; or

    - For all other Generator Cold Weather Constraints, submit within 45 calendar days of determining that the Generator Cold Weather Constraint is applicable.

  - Update the operating limitations under Requirement R1 Part R1.2 if applicable;

  - If the CEA determines the declared Generator Cold Weather Constraint is invalid, update its Corrective Action Plan(s) to require corrective actions be completed in accordance with Requirement R6 or Requirement R7, as applicable, subject to any extensions approved by the CEA or implement freeze protection measures to provide the necessary capability in accordance with Requirement R2;

  - Document and provide notice to the CEA, when a generating unit experiences a Generator Cold Weather Reliability Event with the same cause of a previous Generator Cold Weather Reliability Event at the same or a similar unit, and one or more corrective actions to address the cause is addressed by an existing validated Generator Cold Weather Constraint for the same or a similar unit.

M8. 	Each Generator Owner shall have dated evidence that demonstrates it performed the actions in accordance with Requirement R8. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): a copy of the Generator Cold Weather Constraint declaration, evidence the declaration was provided to the Compliance Enforcement Authority in accordance with the specified timeframe, records that document update(s) to the operating limitations, as needed, updates to the Corrective Action Plan(s), if applicable, and documentation and notice to the CEA of subsequent Generator Cold Weather Reliability Events, if applicable.

Registered Entity Response (Required):

Question: Have any Generator Cold Weather Constraints been declared pursuant to Attachment 1 for applicable EOP-012-3 Requirements ? If Yes, provide a summary of the Generator Cold Weather Constraint(s), reference the applicable Requirement, and the applicable generating unit(s). ☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Entity’s documented process for development of Generator Cold Weather Constraint declarations in accordance with Attachment 1 and the dated declarations (if applicable) for the Entity’s applicable generating unit(s).

Evidence the entity met the submittal timeframes of Requirement R8 Part 8.1 for applicable generating units.

Entity’s updates to capability and availability under Requirement R1 Part R1.2 resulting from a declaration (if applicable.)

Entity’s declaration, and justifications for the declaration, of any Generator Cold Weather Constraint that precludes the Generator Owner from implementing selected action(s) contained within the Corrective Action Plan (if included in the ERO Enterprise CAP Extension and Generator Cold Weather Constraint review process documentation simply provide a listing of submittals (e.g., dates, Align reference number, etc.).) For Generator Cold Weather Constraints not yet submitted, provide the timelines, supporting documentation, and projected submittal dates, if applicable.

Updates to Corrective Action Plans for any invalid, as determined by the CEA, declaration of Generator Cold Weather Constraints.

Evidence the entity documented and provided notice to the CEA when a generating unit experiences a Generator Cold Weather Reliability Event with the same cause of a previous Generator Cold Weather Reliability Event (at the same or similar unit) and is addressed by an existing validated Generator Cold Weather Constraint.

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R8

This section to be completed by the Compliance Enforcement Authority

|  | (Part 8.1.) Verify Generator Cold Weather Constraint submittals meet the timelines in Part 8.1. |
| --- | --- |
|  | (Part 8.2.) Verify operating limitations under Requirement R1 Part R1.2 have been updated (if applicable.) |
|  | Verify date of Corrective Action Plan(s) reflects any review of a Generator Cold Weather Constraint and subsequent change because of the review (if applicable.) |
|  | (Part 8.3.) If a Generator Cold Weather Constraint is determined to be invalid, verify the timelines for the associated Corrective Action Plans have been updated to require corrective actions be completed in accordance with Requirement R6 or Requirement R7, as applicable, subject to any extensions approved by the CEA, or implement freeze protection measures to provide the necessary capability in accordance with Requirement R2. |
|  | (Part 8.4.) If a Generator Owner experiences a Generator Cold Weather Reliability Event with the same cause of a previous Generator Cold Weather Reliability Event at the same or a similar unit, and one or more corrective actions to address the cause is addressed by an existing validated Generator Cold Weather Constraint for the same or a similar unit, verify documentation of these circumstance and that the CEA was provided notice. |
| Note to Auditor: Reasonable justification for Generator Cold Weather Constraints should be provided and considered when reviewing declaration submittals (see the ERO Enterprise CAP Extension and Generator Cold Weather Constraint review process). Generator Cold Weather Constraints should be available to auditor for additional confirmation through Align. An entity may simply provide the Align reference number for a Generator Cold Weather Constraint submittal. Note that “document and provide notice” in Requirement R8 Part 8.4 is managed through the NERC Generator Cold Weather CAP Extension and Constraint process. Corrective Action Plans are dependent upon the ECWT value and Generator Cold Weather Constraints are dependent upon the inability to implement a corrective action. Updates to availability and capability should be provided to the appropriate entities and should be reviewed (note the appropriate functional entity (e.g., RC, TOP, or BA) data specification may dictate timing associated with the provision of data.) Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

R9 Supporting Evidence and Documentation

R9.	The Generator Owner shall review each Generator Cold Weather Constraint declaration validated by the CEA at least once every 36 calendar months to determine if it remains valid in accordance with Attachment 1. [Violation Risk Factor: Lower] [Time Horizon: Long‐term Planning]

9.1 	If a Generator Cold Weather Constraint is determined to be no longer valid, then within six (6) calendar months of such determination, the Generator Owner shall develop or update a Corrective Action Plan pursuant to Requirement R7.

M9. 	Each Generator Owner shall have dated evidence that demonstrates it reviewed Generator Cold Weather Constraints in accordance with Requirement R9. Acceptable evidence may include, but is not limited to, the following dated documentation (electronic or hardcopy format): records that document the performance of the review within the required timeframe, records that demonstrate that a Corrective Action Plan was developed or updated within the required timeframe (if applicable).

Registered Entity Response (Required):

Question: Have any validated Generator Cold Weather Constraints been reviewed within the compliance monitoring timeframe? If Yes, provide a summary of the Generator Cold Weather Constraint(s), the review completed, and the applicable generating unit(s) for which the Generator Cold Weather Constraint was declared.

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Question: Has a validated Generator Cold Weather Constraints been determined to be no longer valid within the compliance monitoring timeframe? If Yes, provide a summary of the Generator Cold Weather Constraint(s), the validation determination status date, the applicable generating unit(s) for which the Generator Cold Weather Constraint was declared, and the Corrective Action Plan for the applicable generating unit(s).

☐ Yes  ☐ No

[Note: A separate spreadsheet or other document may be used. If so, provide the document reference below.]

Compliance Narrative:

Provide a brief explanation, in your own words, of how you comply with this Requirement. References to supplied evidence, including links to the appropriate page, are recommended.

Evidence Requestedi:

Provide the following evidence, or other evidence to demonstrate compliance.

Process documentation, and results of the process, reflecting review of each Generator Cold Weather Constraint declaration at least once every 36 calendar months.

Generator Cold Weather Constraint validation dated evidence (note- may include Align reference information.)

Registered Entity Evidence (Required):

| The following information is requested for each document submitted as evidence. Also, evidence submitted should be highlighted and bookmarked, as appropriate, to identify the exact location where evidence of compliance may be found. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| File Name | Document Title | Revision or Version | Document Date | Relevant Page(s) or Section(s) | Description of Applicability of Document |

Audit Team Evidence Reviewed (This section to be completed by the Compliance Enforcement Authority):

Compliance Assessment Approach Specific to EOP-012-3, R9

This section to be completed by the Compliance Enforcement Authority

|  | (R9.) Verify validation dates of Generator Cold Weather Constraints. |
| --- | --- |
|  | (R9.) Verify the review occurred at least once within 36 calendar months of the validation date for the applicable generating unit(s). |
|  | (Part 9.1.) Verify that if a Generator Cold Weather Constraint is determined to be invalid, a Corrective Action Plan was developed or updated within six (6) calendar months of that determination. |
| Note to Auditor: If a Generator Owner that has a validated Generator Cold Weather Constraint has not been reviewed during the compliance monitoring time period, review Align or other tools for confirmation. Note that Generator Cold Weather Constraints may cover multiple generating units and may be updated periodically. For example, an initial declaration for Unit A was validated in December but additional units were added to a declaration in February (and subsequently validated in March). The timeline for review starts with the initial validation date (i.e., December). An entity may choose, when updating a Generator Cold Weather Constraint with additional units, to review the Generator Cold Weather Constraint and document it accordingly which would reset the 36-calendar month timeframe. Generator Owners should provide evidence reflecting the depth of the review. Generator Cold Weather Constraints may be determined to be no longer valid for various reasons. Key here is the definition of a Generator Cold Weather Constraint is based on the inability to implement a corrective action. Depending upon the nature of the Generator Cold Weather Constraint this could mean a piece of equipment was made available or a new technology has been largely accepted by the industry. Please review the “Abeyance” section within the ‘Additional Information’ portion of this RSAW. |  |

## Auditor Notes:

Additional Information:

Compliance Abeyance Period:

“From the effective date of Reliability Standard EOP-012-3 until October 1, 2027, the Compliance Enforcement Authority will not pursue an action under Sections 4A.0 or 5.0 of Appendix 4C to the Rules of Procedure for a failure to comply with Reliability Standard EOP-012-3 Requirement R1 Part 1.1 with respect to the calculation of the Extreme Cold Weather Temperature for an applicable generating unit, or any other failure to comply resulting from an incorrect calculation of the Extreme Cold Weather Temperature for that generating unit, against any entity acting in good faith to comply with the standard in accordance with the relevant implementation plan. “Good faith” in this context refers to a sincere intention to comply with Reliability Standard EOP-012-3, regarding all requirements based on the calculation of the Extreme Cold Weather Temperature for each applicable generating unit, following a reasonable and serious assessment by the entity in determining how this Reliability Standard should be applied to its particular facts and circumstances. Entities shall participate in any compliance monitoring activities undertaken by the Compliance Enforcement Authority during this abeyance period and submit documentation as requested.”

ERO Enterprise staff will consider the abeyance language and the impact to compliance monitoring efforts to support understanding how entities are implementing the Requirements.

Reliability Standard

The full text of EOP-012-3 may be found on the NERC Web Site (www.nerc.com) under “Program Areas & Departments”, “Reliability Standards.”

In addition to the Reliability Standard, there is an applicable Implementation Plan available on the NERC Web Site.

In addition to the Reliability Standard, there is background information available on the NERC Web Site.

Capitalized terms in the Reliability Standard refer to terms in the NERC Glossary, which may be found on the NERC Web Site.

Sampling Methodology

Sampling is essential for auditing compliance with NERC Reliability Standards since it is not always possible

or practical to test 100% of either the equipment, documentation, or both, associated with the full suite of enforceable standards. The Sampling Methodology Guidelines and Criteria (see NERC website), or sample guidelines, provided by the Electric Reliability Organization help to establish a minimum sample set for monitoring and enforcement uses in audits of NERC Reliability Standards.

Regulatory Language

EOP-012-3 was approved in the following FERC Order: Order Approving Extreme Cold Weather Reliability Standard EOP-012-3 and Directing Data Collection, 192 FERC ¶ 61,229 (2025)

Revision History for RSAW

| Version | Date | Reviewers | Revision Description |
| --- | --- | --- | --- |
| 1 | 10/1/2025 | NERC Compliance Assurance, Operations and Planning Compliance Task Force | New Document |

NERC developed this Reliability Standard Audit Worksheet (RSAW) language in order to facilitate NERC’s and the Regional Entities’ assessment of a registered entity’s compliance with this Reliability Standard. The NERC RSAW language is written to specific versions of each NERC Reliability Standard. Entities using this RSAW should choose the version of the RSAW applicable to the Reliability Standard being assessed. While the information included in this RSAW provides some of the methodology that NERC has elected to use to assess compliance with the Requirements of the Reliability Standard, this document should not be treated as a substitute for the Reliability Standard or viewed as additional Reliability Standard Requirements. In all cases, the Regional Entity should rely on the language contained in the Reliability Standard itself, and not on the language contained in this RSAW, to determine compliance with the Reliability Standard. NERC’s Reliability Standards can be found on NERC’s website. Additionally, NERC Reliability Standards are updated frequently, and this RSAW may not necessarily be updated with the same frequency. Therefore, it is imperative that entities treat this RSAW as a reference document only, and not as a substitute or replacement for the Reliability Standard. It is the responsibility of the registered entity to verify its compliance with the latest approved version of the Reliability Standards, by the applicable governmental authority, relevant to its registration status.

The RSAW may provide a non-exclusive list, for informational purposes only, of examples of the types of evidence a registered entity may produce or may be asked to produce to demonstrate compliance with the Reliability Standard. A registered entity’s adherence to the examples contained within this RSAW does not necessarily constitute compliance with the applicable Reliability Standard, and NERC and the Regional Entity using this RSAW reserve the right to request additional evidence from the registered entity that is not included in this RSAW. This RSAW may include excerpts from FERC Orders and other regulatory references which are provided for ease of reference only, and this document does not necessarily include all applicable Order provisions. In the event of a discrepancy between FERC Orders, and the language included in this document, FERC Orders shall prevail.

Compliance Assessment Date(s): The date(s) the actual compliance assessment (on-site audit, off-site spot check, etc.) occurs.